## System details
System details
Use one log book for each LEV system. Keep it with the system's user manual, its commissioning report and its latest thorough examination and test report.
System details
Company
Site address
System name or ID number
Where the system is (building, room or area)
Process and substances it controls
Hoods (how many, and what type)
Designed and installed by
Commissioning date and report reference
Where the user manual is kept
Person responsible for the system
Months between thorough examinations and tests (14 at most) | 14
Date of the last thorough examination and test
Next thorough examination and test due
Source: HSE leaflet INDG408.

## Check schedule
Check schedule
Set out what to check on each part of the system, how often, and who checks it. Copy the checks and how often they are due from the system's user manual. The filled rows are HSE's examples.
Part of the system | What to check | How often | Who checks
Hoods | Airflow indicator reading, physical damage, blockages, clutter in the way
Ducts | Damage, wear and partial blockage, especially flexible ducts
Dampers | Still in the set position
Air cleaner or filter | Damage, pressure reading across the filter, failure alarms
Fan | Changes in noise or vibration, power use, clean impeller
Operators | Using the system correctly, for example hood position and the work kept inside the capture zone
Source: HSE guidance HSG258, paragraphs 315, 319 and 320.

## Daily check
Daily check by the person using it
Answer each question before use. Write Y for yes or N for no. If question 4 or 5 is a yes, or question 1, 2, 3 or 6 is a no, tell your supervisor straight away.
Question | Mon | Tue | Wed | Thu | Fri | Sat | Sun
Week starting
System name or ID
1. Does the indicator show the LEV is working properly?
2. Is it taking away all the harmful dust, mist, fumes and gas? Remember, some of these may be invisible.
3. Are you close enough to it so it can do its job properly?
4. Are there any signs it is not working properly, like smells or settled dust?
5. Are there any unusual noises or vibration coming from it?
6. Has it been thoroughly tested, with a 'tested' label that is within date?
7. Have you told your supervisor about anything you think may be wrong?
Initials
Source: Questions from HSE pocket card INDG409, Time to clear the air!.
Contains public sector information published by the Health and Safety Executive and licensed under the Open Government Licence.

## Weekly check
Weekly check
HSE's COSHH code of practice and guidance says LEV should be visually checked at least once a week. Write OK, or describe what you found.
Date | Hoods | Airflow indicator reading | Ducts | Dampers | Filter pressure reading | Fan noise and vibration | Used correctly | Faults found and action taken | Name | Signature
Source: HSE L5, paragraph 172, and HSG258, paragraphs 318 and 319.

## Maintenance
Maintenance, replacements and repairs
Record every service, part replaced and repair, planned or not, and who did the work.
Date | Part of the system | Work done | Planned or unplanned | Parts replaced | Done by (name and company) | Signature
Source: HSE guidance HSG258, paragraphs 318 and 319.

## Faults and actions
Faults and actions
Record each fault found by a check or a test, what will put it right, and when it was done. COSHH requires a record of the repairs made as a result of each thorough examination and test.
Date found | Fault | Found by | Action needed | Who will do it | Date done | Signed off by
Source: COSHH Regulations 2002, regulation 9(4).

## Test record
Thorough examination and test record
COSHH requires a thorough examination and test at least once every 14 months, or more often for the processes in its Schedule 4. Keep each full report, and the record of repairs that followed it, for at least five years, with a copy at the workplace.
Test date | Examiner and company | Report reference | Hoods passed | Hoods failed | Critical faults | Repairs completed on | Next test due
Source: COSHH Regulations 2002, regulation 9(2) and (4), and HSG258, paragraph 350.

## Before the test
Before the examiner visits
HSE guidance lists what the examiner should use at each thorough examination and test, where it exists. Tick each one when it is ready.
Before the examiner visits | Done
Test booked for
Examiner and company
Contact on the day
Commissioning report
User manual
This log book
Last thorough examination and test report
Air sampling records, and notes on how operators use the system
Confirmation that the system, the layout and the process have not changed since the last test, or a list of what changed
Source: HSE guidance HSG258, paragraph 334.